[Date]

Faisal A

[Company name]

[Company address]

Academic HVAC Design Report

Contents

1. Project Summary	2

2. Problem Statement	2

2.1. Challenge:	2

3. Design Methodology	2

3.1. Building Modeling & Simulations	2

3.2. System Selection & Optimization	2

3.3. Performance & Environmental Analysis	3

4. Design Parameters	3

5. Innovative Features	3

6.  Visual Results	3

6.1. Peak Load Comparison	3

6.2. Energy Consumption Breakdown	3

6.3. Borehole Layout (Hybrid System)	4

7. Key Takeaways	4

# 1. Project Summary

Designed an efficient HVAC system for a 12-story residential condominium in Toronto, balancing comfort, energy efficiency, and environmental sustainability. The project evaluated conventional systems, GSHP (ground-source heat pump), and hybrid GSHP systems, comparing energy consumption, GHG emissions, and operational costs.

Key Outcomes:

Hybrid GSHP system reduced GHG emissions by ~90% compared to conventional systems

Optimized borehole loop lengths and flow rates for cost-effective geothermal implementation

Achieved balanced indoor comfort across summer and winter design conditions

# 2. Problem Statement

Toronto’s residential buildings face high energy demand for heating and cooling. Conventional HVAC systems contribute to GHG emissions and operational costs.

## 2.1. Challenge:

Design a system capable of handling peak summer and winter loads

Minimize energy consumption and carbon footprint

Incorporate ground-source heat pumps and hybrid approaches

# 3. Design Methodology

## 3.1. Building Modeling & Simulations

Created energy model in eQuest to calculate loads, ventilation, infiltration, and R-values

Simulated indoor comfort under summer and winter design conditions

## 3.2. System Selection & Optimization

Evaluated three options: Conventional, GSHP, and Hybrid GSHP

Optimized GSHP loop lengths and pump sizing using HGS software

## 3.3. Performance & Environmental Analysis

Calculated annual energy consumption and GHG emissions for each system

Compared operational costs and capital investment for feasibility

# 4. Design Parameters

| Parameter | Value |
| --- | --- |
| Peak Cooling Load | 296 kBtu/hr |
| Peak Heating Load | 423 kBtu/hr |
| Annual Electricity (Hybrid GSHP) | 24,929 kWh |
| Annual Gas (Hybrid GSHP) | 479 m³ |
| Total GHG (Hybrid GSHP) | 5,210 kg CO₂ |
| Ventilation | 180 cfm for 12 units |
| Infiltration (Winter, 1 unit) | 34.22 cfm |

# 5. Innovative Features

Hybrid GSHP Optimization: Reduced borehole length from 230 ft (GSHP) to 381 ft with hybrid for cost-effective heating/cooling

Energy Efficiency: Hybrid system cut electricity consumption by ~87,000 kWh annually compared to conventional HVAC

Environmental Impact: Reduced total GHG emissions by ~44,000 kg CO₂ per year

# 6.  Visual Results

6.1. Peak Load Comparison
(Diagram showing conventional vs GSHP vs hybrid peak heating/cooling loads)

## 6.2. Energy Consumption Breakdown

Conventional HVAC → High electricity & gas usage

GSHP → Reduced electricity, zero gas

Hybrid GSHP → Minimal electricity & gas, low operational cost

## 6.3. Borehole Layout (Hybrid System)

Red line → Heating loop

Blue line → Cooling loop

# 7. Key Takeaways

Hybrid GSHP is the optimal balance between cost, energy efficiency, and environmental sustainability

eQuest + HGS simulation enables data-driven HVAC design decisions

Achieved portfolio-worthy design demonstrating mastery of HVAC engineering, energy modeling, and sustainable design principles